2022 Annual Drinking Water Quality Report

(Consumer Confidence Report)

MORÓN AIR BASE, SPAIN

This report contains important information about your drinking water.  If you do not understand it, please have someone explain or translate it for you.

Este informe contiene información importante sobre su agua potable. Si no lo entiende, pídale a alguien que se lo explique o lo traduzca.

Introduction

We are pleased to present this year’s Annual Drinking Water Quality Report (Consumer Confidence Report – CCR) as required by the Final Governing Standards for Spain (FGS-S) and Department of the Air Force Instruction 48-144, Drinking Water Surveillance Program.  This report provides an overview of last year’s (2022) drinking water quality and details about where your water comes from, what it contains, and how it compares to standards set by regulatory agencies.  Our goal is to provide you with a safe, quality, and reliable drinking water supply.  We are committed to providing you with this information because informed customers are the best allies.

Water Sources

The sources of drinking water (both tap water and bottled water) include rivers, lakes, streams, ponds, reservoirs, springs, and wells.  As water travels over the surface of the land or through the ground, it dissolves naturally occurring minerals, and in some cases, radioactive material, and can pick up substances resulting from the presence of animals or from human activity.  In order to ensure that tap water is safe to drink, the final governing standard for Spain prescribes regulations which limit the amount of certain contaminants in drinking water provided by public water systems.  Food and Drug Administration regulations establish limits for contaminants in bottled water which must provide the same protection for public health.

Contaminants that may be present in source water include:

-  Microbial contaminants, such as viruses and bacteria, which may come from sewage treatment plants, septic systems, agricultural livestock operations and wildlife.

-  Inorganic contaminants, such as salts and metals, which can be naturally occurring or result from urban storm water runoff, industrial or domestic wastewater discharges, oil and gas production, mining, or farming.

-  Pesticides and herbicides, which may come from a variety of sources such as agriculture, urban storm water runoff, and residential uses.

-  Organic chemical contaminants, including synthetic and volatile organic chemicals, which are by-products of industrial processes and petroleum production, and can also, come from gas stations, urban storm water runoff, and septic systems.

-  Radioactive contaminants, which can be naturally occurring or be the result of oil and gas production and mining activities.

Where Do We Get Our Drinking Water?

Morón AB receives its water supply from a shallow regional aquifer.  Ground water that is not under the influence of superficial waters is the primary source of the water system.  Six well fields pump water through a water treatment plant to a comprehensive distribution system.  The water is treated using reverse osmosis and granular activated carbon to remove contaminants prior to disinfection with chlorine.  The water system supplies water to all facilities including the Youth Center, Military Family Housing, DoDEA School, dorms, dining facilities, clinic and most Spanish Air Force facilities.

Drinking Water and Your Health

All drinking water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants.  The presence of contaminants does not necessarily indicate that the water poses a health risk.  More information on contaminants and potential health effects can be obtained by calling Bioenvironmental Engineering (BE) at DSN 479-2220 (0049-6371-46-2220).  Some people may be more vulnerable to contaminants in drinking water than the general population.  Immunocompromised individuals such as those with cancer undergoing chemotherapy, those who have undergone organ transplants, those with HIV/AIDS or other immune system disorders, some elderly, and infants are at a higher risk of waterborne illness.  These people should seek advice about drinking water from their health care providers. EPA/CDC guidelines on appropriate means to lessen the risk of infection by Cryptosporidium and other microbial contaminants are available from the Safe Drinking Water Hotline (800-426-4791).

Is there Lead in my Water?

Although we regularly test lead levels in your drinking water, it is possible that lead and/or copper levels at your home are higher because of materials used in your plumbing.  If present, elevated levels of lead can cause serious problems, especially for pregnant women and young children.  Lead in drinking water is primarily from materials and components associated with service lines and home plumbing.  MorÓn AB is responsible for providing high quality drinking water but cannot control the variety of materials used in plumbing components.  When your water has been sitting for several hours, you can minimize the potential for lead and copper exposure by flushing your tap for 30 seconds to 2 minutes before using water for drinking or cooking.  If you are concerned about lead in your water, you may wish to have your water tested.  Information on lead in drinking water, testing methods, and steps you can take to minimize exposure is available from the Safe Drinking Water Hotline at 1-800-426-4791 or http://www.epa.gov/safewater/lead.

Has MorÓn AB tested its Water for PFAS?

Per- and polyfluoroalkyl substances (PFAS) are a group of man-made chemicals that includes PFOS and PFOA.  PFAS have been manufactured and used in a variety of industries around the globe, including in the United States, since the 1940s.  PFAS are found in everyday consumer items, from nonstick cookware to water-resistant clothing.  They are also found in certain firefighting foam (AFFF).  PFOS and PFOA have been the most extensively produced and studied of the PFAS chemicals.

In May 2016, the EPA issued Safe Drinking Water Act (SDWA) lifetime Health Advisories (HA) recommending the individual or combined levels of PFOS and PFOA in drinking water be at or below 70 parts per trillion.  This HA offers a margin of protection from adverse health effects over a lifetime of exposure to PFOS and PFOA in drinking water.  Additional information about PFAS can be found at https://www.epa.gov/pfas.

PFAS was detected but PFOS/PFOA were below the 2016 EPA HA

On 13 March 2022 samples were collected from building 525, water tower.  We are informing you that 6 of the 18 PFAS compounds covered by the sampling method were detected above the method reporting limit (MRL).  The results are provided in Table Unregulated Contaminants (page 7).  The EPA does not have a HA for all of the compounds at this time.  PFOA and PFOS were detected but below the 2016 EPA HA.  As PFOA and PFOS were below the 2016 EPA HA, there is no immediate cause for concern, but we will continue to monitor the drinking water closely.  In accordance with DoD policy AF-Owned PFAS Sampling Policy & Implementation Guidance, March 2020, Morόn AB will collect quarterly samples for PFAS for one year and then every two years thereafter as long as the results are below the 2016 EPA HA.

A Final Word on Water Quality

Your water quality team at Morón AB works around the clock to provide safe, dependable water at every tap.   But they can only ensure the success of today’s mission if everyone contributes.  Tomorrow’s success will depend on all of us, working together, to protect our vital water resources.

Remember, the water we use does not quickly return to the aquifer, but is, for the most part, “consumed” by our actions.  Morón AB and many nearby villages draw water from the same aquifer.  Conservation is therefore essential to protect our water supply.

You should also consider ways you can reduce your water consumption, i.e., don’t let the water run while brushing your teeth, take a shower vs. a bath.  There are numerous ways to save our most valuable natural resource for us and the future of our children.  If you have ideas to reduce usage and contamination of this valuable resource submit it to the Ramstein AB Drinking Water Quality Working Group via Morón AB IDMTs.  These efforts will help protect the future water supply by reducing the overall consumptive use.

Customer Reviews Welcome

We are available to address any questions or concerns you may have.  Housing residents should contact the Housing Office with any water concerns.  Dorm residents should contact their building manager.

For more information on this report or base drinking water quality, please call BE at DSN 479-2220 (0049-6371-462220), the 86 CES Environmental Management Flight at DSN 480-7712, or 496 ABS IDMTs at 722-8069.

About the Following Pages

The tables below list all of the drinking water contaminants that we detected during the calendar year of this report.  Although more than 80 contaminants were tested, only those substances listed below were detected in our water.  The FGS-S requires us to monitor for certain contaminants less than once per year because the concentrations of these contaminants do not vary significantly from year to year, or the system is not considered vulnerable to this type of contamination.

Definitions and Abbreviations

Action Level (AL):  The concentration of a contaminant which, if exceeded, triggers treatment or other requirements which a water system must follow.

Average:  Regulatory compliance with some MCLs are based on running annual average of monthly samples.

Maximum Contaminant Level (MCL):  The highest level of a contaminant that is allowed in drinking water.  MCLs are set as close to the MCLGs as feasible using the best available treatment technology.

Maximum Contaminant Level Goal (MCLG):  The level of a contaminant in drinking water below which there is no known or expected risk to health.   MCLGs allow for a margin of safety.

Maximum Residual Disinfectant Level (MRDL):  The highest level of disinfectant allowed in drinking water.  There is convincing evidence that addition of a disinfectant is necessary for control of microbial contaminants.

Maximum Residual Disinfectant Level Goal (MRDLG):  The level of a drinking water disinfectant below which there is no known or expected risk to health.  MRDLGs do not reflect the benefits of the use of disinfectants to control microbial contamination.

ppm:  milligrams per liter (mg/L) or parts per million – or one ounce in 7,350 gallons of water.

How to Read the Data Tables

Starting with a substance, read across.  Year sampled is 2022.  MCL shows the highest level of substance (contaminant) allowed.  MCLG is the goal level for that substance (this may be lower than what is allowed). Average Amount Detected represents the measured amount (less is better).  Range tells the highest and lowest amounts measured.  A ‘No’ under Violation means the amount of the substance met government requirements. Typical Source tells where the substance usually originates.  Unregulated substances are measured, but maximum allowed contaminant levels have not been established by the government.

Water Quality Results

| Residual Disinfectants | Unit of Measure | MRDL | MRDLG | Average Level | Minimum Level | Maximum Level | Violation | Typical Source |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Free Available Chlorine | ppb | 4000 | 4000 | 1960 | 200 | 3400 | No | Water additives used to control microbes |
| Contaminant | Unit of Measure | MCLG | MCL | Level Found | Violation | Typical Source |
| Total Coliform | # of Positives | 0 | 5.0% | 0 | No | Naturally present in the environment |
| Barium | ppb | 2000 | 2000 | 9 | No | Discharge of drilling wastes; discharge from metal refineries; erosion of natural deposits |
| Bromate | ppb | 0 | 10 | 5.7 | Yes | By-product of drinking water disinfection |
| Nitrate | ppb | 10000 | 10000 | 6600 | No | Runoff from fertilizer use; leaking from septic tanks, sewage; erosion of natural deposits |
| Nitrite | ppb | 1000 | 1000 | <10 | No | Runoff from fertilizer use; leaking from septic tanks, sewage; erosion of natural deposits |
| Total Trihalomethanes | ppb | 80 | 80 | 2.0 | No | By-products of drinking water chlorination |

| Lead and Copper | Units | MCLG | MCL | Level Found | 90th Percentile | # Sites Over AL | Violation | Typical Source |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Lead | ppb | 0 | 10 | < 1 | 1 | 0 | No | Corrosion of household plumbing systems; erosion of natural deposits |
| Copper | ppb | 1300 | 1300 | 1 | 1 | 0 | No | Erosion of natural deposits; leaching from wood preservatives; corrosion of household plumbing systems |

| Unregulated Contaminants | Unit | MCLG | MCL | Level Found | Violation | Typical Source |
| --- | --- | --- | --- | --- | --- | --- |
| Perfluorobutanesulfonic Acid (PFBS) | ppt | 0 | N/A | 6.4 | No | Aqueous Film-Forming Foam (AFFF) used for fire suppression; industrial chemicals; consumer goods |
| Perfluoroheptanoic Acid (PFHpA) | ppt | 0 | N/A | 9.6 | No |  |
| Perfluorohexanesulfonic Acid (PFHxS) | ppt | 0 | N/A | 32 | No |  |
| Perfluorohexanoic Acid (PFHxA) | ppt | 0 | N/A | 23 | No |  |
| Perfluorooctanesulfonic Acid (PFOS) | ppt | 0 | 70 | 5.6 | No |  |
| Perfluorooctanoic Acid (PFOA) | ppt | 0 | 70 | 9.2 | No |  |

Violations

| Bromate |
| --- |
| A lifetime of drinking bromate at higher levels has an increased lifetime cancer risk of 2 in 10,000. Some people who ingested large amounts of bromate had gastrointestinal symptoms such as nausea, vomiting, diarrhea and abdominal pain. Some individuals who ingested very high concentrations of bromate also experienced adverse effects in kidney, nervous system, and hearing loss. However, these people were exposed to bromate levels thousands of times the amount the amount in the FGS-S. |
| Violation Type | Violation Begin | Violation End | Violation Explanation |
| MCL | 10 October 2019 | TBD | BE performed sampling of the Morón Air Base drinking water system for Bromates on 10 October 2019. Bromate levels from this monitoring event were found to be in exceedance of 0.01 mg/L (equivalent to ppm) of the MCL. Bromate is a byproduct of the water treatment disinfection process and we believe the exceedance of Bromate is due to the high level of free available chlorine (FAC) in the water system for CY2019. While not over the MCL of 4000 ppb, the levels of FAC were greater than the recommended limits of 200-600 ppb. Working with Morón Air Base CE Water Production Shop personnel, we have reduced the level of FAC to the recommended level for the installation. Also, we have put a process in place to verify the FAC to be in the recommended limits before collecting the water samples to analyze for bromate. In an effort to provide statistical data and/or provide a data trend, the BE office will continue to sample for bromate on a quarterly basis. This also serves as a precautionary measure to detect any changes in bromate levels more expediently. This is not driven by regulatory requirement. Levels have been acceptable since original violation. Violation ends when four consecutive quarterly samples have a resulting running average below the MCL. Four consecutive samples have not yet been accomplished. |

| Tier 3 Violation - Failure to Conduct Sampling in 4th Quarter of 2022 |
| --- |
| A Tier 3 violation occurs when a water system violates a standard that does not have a direct impact on human health. The water supplier has one year to provide notice to customers. In the fourth quarter of 2022, sampling did not occur for Synthetic Organics, Disinfection Byproducts, Inorganics, or Radiologicals. - Some people who drink water containing Synthetic Organics in excess of the MCL over many years could experience problems with their cardiovascular system or reproductive difficulties. - Some people who drink water containing Inorganics in excess of the MCL over many years could experience skin damage or problems with their circulatory system and may have an increased risk of getting cancer. - Certain minerals are radioactive and may emit forms of radiation known as photons and beta radiation. Some people who drink water containing alpha, beta and photon emitters in excess of the MCL over many years may have an increased risk of getting cancer. |
| Violation Type | Violation Begin | Violation End | Violation Explanation |
| Monitoring | 31 Dec 2022 | TBD | During the fourth quarter of 2022, BE did not perform any quarterly sampling for the following analytes: Synthetic Organics, Disinfection Byproducts, Inorganics, and Radiologicals. This violation affects Moron AB only. Past sampling for these analytes has not shown a trend at or in excess of the MCL. First quarter sampling for 2023 will be completed and this violation will be corrected. |